## RCA
date | T+1 | T+2 | Abnormal weather factor | T+1 model under/overforecast reason | T+2 model under/overforecast reason | Reason why it happen | Ask SLDC | Assumption / Learning | t1_accuracy_pct | t2_accuracy_pct | actual_mean_mw | actual_peak_mw | temp_max_c | humidity_mean_pct | rain_sum_mm | wind_max | heat_index_proxy
2026-04-01 | 96.14% accuracy | 89.00% accuracy | No clear abnormal weather factor from fetched weather versus trailing 7-day context. | T+1: no block-level forecast rows available; daily summary only. | T+2: no block-level forecast rows available; daily summary only. | No clear abnormal weather factor from fetched weather versus trailing 7-day context. T+1: no block-level forecast rows available; daily summary only. T+2: no block-level forecast rows available; daily summary only. Actual load had sharp ramp of 588 MW between 15-minute blocks. No block-level forecast rows available in workbook for this date; only daily summary is available. | Confirm whether any non-weather operational event occurred: outage, feeder shutdown, industry holiday, grid restriction, or schedule revision. | Apply ramp-aware forecast limit before export and monitor ramp misses. | 96.14 | 89 | 6424.9135 | 8054.46 | 30.7591 | 59.5083 | 0.045455 | 10.4909 | 49.0633
2026-04-02 | 95.75% accuracy | 93.34% accuracy | No clear abnormal weather factor from fetched weather versus trailing 7-day context. | T+1: no block-level forecast rows available; daily summary only. | T+2: no block-level forecast rows available; daily summary only. | No clear abnormal weather factor from fetched weather versus trailing 7-day context. T+1: no block-level forecast rows available; daily summary only. T+2: no block-level forecast rows available; daily summary only. Actual load had sharp ramp of 534 MW between 15-minute blocks. No block-level forecast rows available in workbook for this date; only daily summary is available. | Confirm whether any non-weather operational event occurred: outage, feeder shutdown, industry holiday, grid restriction, or schedule revision. | Apply ramp-aware forecast limit before export and monitor ramp misses. | 95.75 | 93.34 | 6807.5596 | 8635.01 | 33.0455 | 52.4344 | 0.21364 | 8.6136 | 50.3726
2026-04-03 | 96.18% accuracy | 96.17% accuracy | Rain abnormality: daily rain 1.3 mm, +0.7 mm vs trailing 7d. | T+1: no block-level forecast rows available; daily summary only. | T+2: no block-level forecast rows available; daily summary only. | Rain abnormality: daily rain 1.3 mm, +0.7 mm vs trailing 7d. T+1: no block-level forecast rows available; daily summary only. T+2: no block-level forecast rows available; daily summary only. Actual load had sharp ramp of 597 MW between 15-minute blocks. No block-level forecast rows available in workbook for this date; only daily summary is available. |  | Avoid double counting rain; use one weather channel plus regime flag. Apply ramp-aware forecast limit before export and monitor ramp misses. | 96.18 | 96.17 | 6659.6716 | 7668.67 | 29.4318 | 62.0961 | 1.3045 | 13.2545 | 47.7078
2026-04-04 | 95.20% accuracy | 94.83% accuracy | Rain abnormality: daily rain 1.2 mm, +0.6 mm vs trailing 7d. | T+1: no block-level forecast rows available; daily summary only. | T+2: no block-level forecast rows available; daily summary only. | Rain abnormality: daily rain 1.2 mm, +0.6 mm vs trailing 7d. T+1: no block-level forecast rows available; daily summary only. T+2: no block-level forecast rows available; daily summary only. Actual load had sharp ramp of 535 MW between 15-minute blocks. Weekend profile can differ from weekday industrial/agricultural consumption. No block-level forecast rows available in workbook for this date; only daily summary is available. |  | Avoid double counting rain; use one weather channel plus regime flag. Apply ramp-aware forecast limit before export and monitor ramp misses. Keep separate weekday/weekend bias tables. | 95.2 | 94.83 | 6543.2247 | 8414.08 | 28.4045 | 65.2652 | 1.2455 | 9.1773 | 46.9428
2026-04-05 | 91.77% accuracy | 89.00% accuracy | No clear abnormal weather factor from fetched weather versus trailing 7-day context. | T+1: no block-level forecast rows available; daily summary only. | T+2: no block-level forecast rows available; daily summary only. | No clear abnormal weather factor from fetched weather versus trailing 7-day context. T+1: no block-level forecast rows available; daily summary only. T+2: no block-level forecast rows available; daily summary only. Actual average load was 13.3% lower than trailing 7-day level. Actual load had sharp ramp of 606 MW between 15-minute blocks. Weekend profile can differ from weekday industrial/agricultural consumption. No block-level forecast rows available in workbook for this date; only daily summary is available. | Confirm whether any non-weather operational event occurred: outage, feeder shutdown, industry holiday, grid restriction, or schedule revision. | Adaptive baseline should exclude anomaly days and shorten window in April-June. Apply ramp-aware forecast limit before export and monitor ramp misses. Keep separate weekday/weekend bias tables. | 91.77 | 89 | 5669.696 | 7239.37 | 29.1182 | 54.6546 | 0.59545 | 12.0091 | 45.0326
2026-04-06 | 93.45% accuracy | 91.00% accuracy | No clear abnormal weather factor from fetched weather versus trailing 7-day context. | T+1: no block-level forecast rows available; daily summary only. | T+2: no block-level forecast rows available; daily summary only. | No clear abnormal weather factor from fetched weather versus trailing 7-day context. T+1: no block-level forecast rows available; daily summary only. T+2: no block-level forecast rows available; daily summary only. Actual load had sharp ramp of 699 MW between 15-minute blocks. No block-level forecast rows available in workbook for this date; only daily summary is available. | Confirm whether any non-weather operational event occurred: outage, feeder shutdown, industry holiday, grid restriction, or schedule revision. | Apply ramp-aware forecast limit before export and monitor ramp misses. | 93.45 | 91 | 6333.5422 | 8652.28 | 30.5182 | 45.7727 | 0.063636 | 10.9182 | 44.4872
2026-04-07 | 89.20% accuracy | 93.80% accuracy | Rain abnormality: daily rain 8.4 mm, +7.7 mm vs trailing 7d. Wind abnormality: max wind 16.6, +5.6 vs trailing 7d. | T+1: no block-level forecast rows available; daily summary only. | T+2: no block-level forecast rows available; daily summary only. | Rain abnormality: daily rain 8.4 mm, +7.7 mm vs trailing 7d. Wind abnormality: max wind 16.6, +5.6 vs trailing 7d. T+1: no block-level forecast rows available; daily summary only. T+2: no block-level forecast rows available; daily summary only. Actual load had sharp ramp of 593 MW between 15-minute blocks. No block-level forecast rows available in workbook for this date; only daily summary is available. | Confirm whether any non-weather operational event occurred: outage, feeder shutdown, industry holiday, grid restriction, or schedule revision. | Avoid double counting rain; use one weather channel plus regime flag. Keep wind as diagnostic unless load drop is proven in backtest. Apply ramp-aware forecast limit before export and monitor ramp misses. | 89.2 | 93.8 | 6274.1687 | 8044.39 | 26.7955 | 64.0369 | 8.4273 | 16.6045 | 43.9544
2026-04-08 | 95.80% accuracy | 88.00% accuracy | Humidity abnormality: mean humidity 70.6%, +12.9 points vs trailing 7d. Rain abnormality: daily rain 6.1 mm, +4.4 mm vs trailing 7d. | T+1: no block-level forecast rows available; daily summary only. | T+2: no block-level forecast rows available; daily summary only. | Humidity abnormality: mean humidity 70.6%, +12.9 points vs trailing 7d. Rain abnormality: daily rain 6.1 mm, +4.4 mm vs trailing 7d. T+1: no block-level forecast rows available; daily summary only. T+2: no block-level forecast rows available; daily summary only. Actual average load was 9.4% lower than trailing 7-day level. Actual load had sharp ramp of 635 MW between 15-minute blocks. No block-level forecast rows available in workbook for this date; only daily summary is available. | Confirm whether any non-weather operational event occurred: outage, feeder shutdown, industry holiday, grid restriction, or schedule revision. | Treat humidity as a heat-load amplifier, not only a standalone linear feature. Avoid double counting rain; use one weather channel plus regime flag. Adaptive baseline should exclude anomaly days and shorten window in April-June. Apply ramp-aware forecast limit before export and monitor ramp misses. | 95.8 | 88 | 5786.6686 | 8155.86 | 25 | 70.5781 | 6.0636 | 12.2636 | 42.6445
2026-04-09 | 95.75% accuracy | 87.29% accuracy | No clear abnormal weather factor from fetched weather versus trailing 7-day context. | T+1: model overforecast on average by 195 MW energy error +3.2%. Overforecast blocks 66%. Worst segment: afternoon/ramp (11.0% segment MAPE). No strong weather abnormality; overforecast likely from high baseline or excessive positive bias correction. | T+2: model overforecast on average by 642 MW energy error +10.6%. Overforecast blocks 89%. Worst segment: morning (26.9% segment MAPE). No strong weather abnormality; overforecast likely from high baseline or excessive positive bias correction. | No clear abnormal weather factor from fetched weather versus trailing 7-day context. T+1: model overforecast on average by 195 MW energy error +3.2%. Overforecast blocks 66%. Worst segment: afternoon/ramp (11.0% segment MAPE). No strong weather abnormality; overforecast likely from high baseline or excessive positive bias correction. T+2: model overforecast on average by 642 MW energy error +10.6%. Overforecast blocks 89%. Worst segment: morning (26.9% segment MAPE). No strong weather abnormality; overforecast likely from high baseline or excessive positive bias correction. Actual load had sharp ramp of 675 MW between 15-minute blocks. T+1 worst error is in afternoon/ramp blocks; over-forecast dominates. T+2 highest MAPE segment is morning; over-forecast dominates. | Confirm whether any non-weather operational event occurred: outage, feeder shutdown, industry holiday, grid restriction, or schedule revision. | Apply ramp-aware forecast limit before export and monitor ramp misses. Tune afternoon ramp weights around blocks 52-68. | 95.7468 | 87.2932 | 6052.8601 | 8293.93 | 28.0727 | 57.8641 | 0.96364 | 14.5136 | 44.3168
2026-04-10 | 94.47% accuracy | 91.50% accuracy | Wind abnormality: max wind 22.5, +9.8 vs trailing 7d. | T+1: model overforecast on average by 169 MW energy error +2.7%. Overforecast blocks 53%. Worst segment: afternoon/ramp (13.1% segment MAPE). Wind/storm conditions may have reduced load or shifted demand. | T+2: model overforecast on average by 310 MW energy error +5.0%. Overforecast blocks 69%. Worst segment: afternoon/ramp (20.0% segment MAPE). Wind/storm conditions may have reduced load or shifted demand. | Wind abnormality: max wind 22.5, +9.8 vs trailing 7d. T+1: model overforecast on average by 169 MW energy error +2.7%. Overforecast blocks 53%. Worst segment: afternoon/ramp (13.1% segment MAPE). Wind/storm conditions may have reduced load or shifted demand. T+2: model overforecast on average by 310 MW energy error +5.0%. Overforecast blocks 69%. Worst segment: afternoon/ramp (20.0% segment MAPE). Wind/storm conditions may have reduced load or shifted demand. Actual load had sharp ramp of 666 MW between 15-minute blocks. T+1 worst error is in afternoon/ramp blocks; over-forecast dominates. T+2 worst error is in afternoon/ramp blocks; over-forecast dominates. | Confirm whether any non-weather operational event occurred: outage, feeder shutdown, industry holiday, grid restriction, or schedule revision. | Keep wind as diagnostic unless load drop is proven in backtest. Apply ramp-aware forecast limit before export and monitor ramp misses. Tune afternoon ramp weights around blocks 52-68. | 94.4713 | 91.4998 | 6201.5895 | 8705.45 | 30.5 | 45.705 | 0 | 22.4727 | 44.44
2026-04-11 | 96.14% accuracy | 96.38% accuracy | No clear abnormal weather factor from fetched weather versus trailing 7-day context. | T+1: model underforecast on average by 227 MW energy error -3.5%. Underforecast blocks 92%. Worst segment: afternoon/ramp (6.9% segment MAPE). Weather does not explain the miss; likely baseline, live-bias, holiday, feeder, or industrial schedule issue. | T+2: model underforecast on average by 137 MW energy error -2.1%. Underforecast blocks 68%. Worst segment: night (5.0% segment MAPE). Weather does not explain the miss; likely baseline, live-bias, holiday, feeder, or industrial schedule issue. | No clear abnormal weather factor from fetched weather versus trailing 7-day context. T+1: model underforecast on average by 227 MW energy error -3.5%. Underforecast blocks 92%. Worst segment: afternoon/ramp (6.9% segment MAPE). Weather does not explain the miss; likely baseline, live-bias, holiday, feeder, or industrial schedule issue. T+2: model underforecast on average by 137 MW energy error -2.1%. Underforecast blocks 68%. Worst segment: night (5.0% segment MAPE). Weather does not explain the miss; likely baseline, live-bias, holiday, feeder, or industrial schedule issue. Actual average load was 7.5% higher than trailing 7-day level. Actual load had sharp ramp of 746 MW between 15-minute blocks. Weekend profile can differ from weekday industrial/agricultural consumption. T+1 worst error is in afternoon/ramp blocks; under-forecast dominates. T+2 error concentrated in night blocks; under-forecast bias visible. |  | Adaptive baseline should exclude anomaly days and shorten window in April-June. Apply ramp-aware forecast limit before export and monitor ramp misses. Keep separate weekday/weekend bias tables. Tune afternoon ramp weights around blocks 52-68. Maintain dedicated T+2 night correction for blocks 1-32. | 96.1434 | 96.379 | 6580.9659 | 8824.4 | 31.2364 | 42.8783 | 0.10455 | 13.1 | 44.63
2026-04-12 | 91.68% accuracy | 86.98% accuracy | Heat abnormality: max temp 32.8C, +4.0C vs trailing 7d. Apparent-temperature abnormality: 31.4C, +3.4C vs trailing 7d. | T+1: model overforecast on average by 352 MW energy error +6.2%. Overforecast blocks 72%. Worst segment: afternoon/ramp (18.5% segment MAPE). Weather was hot/humid, so overforecast points to correction stacking or baseline too high. | T+2: model overforecast on average by 389 MW energy error +6.8%. Overforecast blocks 68%. Worst segment: afternoon/ramp (24.0% segment MAPE). Weather was hot/humid, so overforecast points to correction stacking or baseline too high. | Heat abnormality: max temp 32.8C, +4.0C vs trailing 7d. Apparent-temperature abnormality: 31.4C, +3.4C vs trailing 7d. T+1: model overforecast on average by 352 MW energy error +6.2%. Overforecast blocks 72%. Worst segment: afternoon/ramp (18.5% segment MAPE). Weather was hot/humid, so overforecast points to correction stacking or baseline too high. T+2: model overforecast on average by 389 MW energy error +6.8%. Overforecast blocks 68%. Worst segment: afternoon/ramp (24.0% segment MAPE). Weather was hot/humid, so overforecast points to correction stacking or baseline too high. Actual average load was 6.7% lower than trailing 7-day level. Actual load had sharp ramp of 700 MW between 15-minute blocks. Weekend profile can differ from weekday industrial/agricultural consumption. T+1 worst error is in afternoon/ramp blocks; over-forecast dominates. T+2 worst error is in afternoon/ramp blocks; over-forecast dominates. | Confirm whether any non-weather operational event occurred: outage, feeder shutdown, industry holiday, grid restriction, or schedule revision. | Use nonlinear cooling-load and heat-index multipliers for April-June afternoons. Track apparent temperature separately from dry-bulb temperature. Adaptive baseline should exclude anomaly days and shorten window in April-June. Apply ramp-aware forecast limit before export and monitor ramp misses. Keep separate weekday/weekend bias tables. Tune afternoon ramp weights around blocks 52-68. | 91.6849 | 86.9777 | 5719.2825 | 7626.24 | 32.75 | 39.9503 | 0.040909 | 17.7364 | 45.8337
2026-04-13 | 96.06% accuracy | 94.40% accuracy | Heat abnormality: max temp 34.1C, +4.8C vs trailing 7d. Apparent-temperature abnormality: 32.5C, +4.1C vs trailing 7d. | T+1: model overforecast on average by 183 MW energy error +2.8%. Overforecast blocks 71%. Worst segment: afternoon/ramp (8.1% segment MAPE). Weather was hot/humid, so overforecast points to correction stacking or baseline too high. | T+2: model overforecast on average by 160 MW energy error +2.4%. Overforecast blocks 68%. Worst segment: afternoon/ramp (9.8% segment MAPE). Weather was hot/humid, so overforecast points to correction stacking or baseline too high. | Heat abnormality: max temp 34.1C, +4.8C vs trailing 7d. Apparent-temperature abnormality: 32.5C, +4.1C vs trailing 7d. T+1: model overforecast on average by 183 MW energy error +2.8%. Overforecast blocks 71%. Worst segment: afternoon/ramp (8.1% segment MAPE). Weather was hot/humid, so overforecast points to correction stacking or baseline too high. T+2: model overforecast on average by 160 MW energy error +2.4%. Overforecast blocks 68%. Worst segment: afternoon/ramp (9.8% segment MAPE). Weather was hot/humid, so overforecast points to correction stacking or baseline too high. Actual average load was 6.6% higher than trailing 7-day level. Actual load had sharp ramp of 749 MW between 15-minute blocks. T+1 worst error is in afternoon/ramp blocks; over-forecast dominates. T+2 worst error is in afternoon/ramp blocks; over-forecast dominates. |  | Use nonlinear cooling-load and heat-index multipliers for April-June afternoons. Track apparent temperature separately from dry-bulb temperature. Adaptive baseline should exclude anomaly days and shorten window in April-June. Apply ramp-aware forecast limit before export and monitor ramp misses. Tune afternoon ramp weights around blocks 52-68. | 96.0585 | 94.4013 | 6538.657 | 9011.4 | 34.1091 | 33.0012 | 0 | 14.7545 | 45.3655
2026-04-14 | 97.30% accuracy | 96.24% accuracy | Heat abnormality: max temp 36.3C, +6.5C vs trailing 7d. Apparent-temperature abnormality: 35.5C, +6.8C vs trailing 7d. | T+1: model underforecast on average by 104 MW energy error -1.5%. Underforecast blocks 77%. Worst segment: evening (4.7% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. | T+2: model overforecast on average by 28 MW energy error +0.4%. Overforecast blocks 59%. Worst segment: night (4.7% segment MAPE). Weather was hot/humid, so overforecast points to correction stacking or baseline too high. | Heat abnormality: max temp 36.3C, +6.5C vs trailing 7d. Apparent-temperature abnormality: 35.5C, +6.8C vs trailing 7d. T+1: model underforecast on average by 104 MW energy error -1.5%. Underforecast blocks 77%. Worst segment: evening (4.7% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. T+2: model overforecast on average by 28 MW energy error +0.4%. Overforecast blocks 59%. Worst segment: night (4.7% segment MAPE). Weather was hot/humid, so overforecast points to correction stacking or baseline too high. Actual average load was 12.7% higher than trailing 7-day level. Actual load had sharp ramp of 707 MW between 15-minute blocks. Holiday/bridge-day effect likely changed normal working-day profile. T+1 highest MAPE segment is evening; under-forecast dominates. T+2 error concentrated in night blocks; over-forecast bias visible. |  | Use nonlinear cooling-load and heat-index multipliers for April-June afternoons. Track apparent temperature separately from dry-bulb temperature. Adaptive baseline should exclude anomaly days and shorten window in April-June. Apply ramp-aware forecast limit before export and monitor ramp misses. Keep Haryana/national holiday and bridge-day profile classes. Maintain dedicated T+2 night correction for blocks 1-32. | 97.2989 | 96.2381 | 6944.8221 | 9177.37 | 36.2955 | 31.9756 | 0 | 11.9773 | 47.9011
2026-04-15 | 97.44% accuracy | 93.99% accuracy | Heat abnormality: max temp 37.5C, +6.3C vs trailing 7d. Apparent-temperature abnormality: 35.8C, +5.6C vs trailing 7d. | T+1: model underforecast on average by 189 MW energy error -2.6%. Underforecast blocks 94%. Worst segment: evening (3.8% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. | T+2: model underforecast on average by 444 MW energy error -6.1%. Underforecast blocks 100%. Worst segment: afternoon/ramp (7.0% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. | Heat abnormality: max temp 37.5C, +6.3C vs trailing 7d. Apparent-temperature abnormality: 35.8C, +5.6C vs trailing 7d. T+1: model underforecast on average by 189 MW energy error -2.6%. Underforecast blocks 94%. Worst segment: evening (3.8% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. T+2: model underforecast on average by 444 MW energy error -6.1%. Underforecast blocks 100%. Worst segment: afternoon/ramp (7.0% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. Actual average load was 16.4% higher than trailing 7-day level. Actual load had sharp ramp of 745 MW between 15-minute blocks. T+2 worst error is in afternoon/ramp blocks; under-forecast dominates. | Confirm whether any non-weather operational event occurred: outage, feeder shutdown, industry holiday, grid restriction, or schedule revision. | Use nonlinear cooling-load and heat-index multipliers for April-June afternoons. Track apparent temperature separately from dry-bulb temperature. Adaptive baseline should exclude anomaly days and shorten window in April-June. Apply ramp-aware forecast limit before export and monitor ramp misses. Tune afternoon ramp weights around blocks 52-68. | 97.4412 | 93.9882 | 7287.3887 | 9430.46 | 37.4682 | 29.4534 | 0 | 15.4818 | 48.5038
2026-04-16 | 97.26% accuracy | 95.56% accuracy | Heat abnormality: max temp 38.7C, +5.8C vs trailing 7d. Apparent-temperature abnormality: 38.1C, +6.5C vs trailing 7d. | T+1: model underforecast on average by 138 MW energy error -1.8%. Underforecast blocks 67%. Worst segment: afternoon/ramp (3.8% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. | T+2: model underforecast on average by 307 MW energy error -4.0%. Underforecast blocks 85%. Worst segment: afternoon/ramp (5.8% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. | Heat abnormality: max temp 38.7C, +5.8C vs trailing 7d. Apparent-temperature abnormality: 38.1C, +6.5C vs trailing 7d. T+1: model underforecast on average by 138 MW energy error -1.8%. Underforecast blocks 67%. Worst segment: afternoon/ramp (3.8% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. T+2: model underforecast on average by 307 MW energy error -4.0%. Underforecast blocks 85%. Worst segment: afternoon/ramp (5.8% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. Actual average load was 15.5% higher than trailing 7-day level. Actual load had sharp ramp of 680 MW between 15-minute blocks. T+1 worst error is in afternoon/ramp blocks; under-forecast dominates. T+2 worst error is in afternoon/ramp blocks; under-forecast dominates. |  | Use nonlinear cooling-load and heat-index multipliers for April-June afternoons. Track apparent temperature separately from dry-bulb temperature. Adaptive baseline should exclude anomaly days and shorten window in April-June. Apply ramp-aware forecast limit before export and monitor ramp misses. Tune afternoon ramp weights around blocks 52-68. | 97.2614 | 95.5626 | 7479.8955 | 9618.54 | 38.6818 | 29.411 | 0 | 12.8727 | 50.0585
2026-04-17 | 93.86% accuracy | 92.73% accuracy | Heat abnormality: max temp 37.7C, +3.3C vs trailing 7d. Apparent-temperature abnormality: 36.8C, +3.7C vs trailing 7d. | T+1: model overforecast on average by 163 MW energy error +2.1%. Overforecast blocks 58%. Worst segment: evening (11.6% segment MAPE). Weather was hot/humid, so overforecast points to correction stacking or baseline too high. | T+2: model underforecast on average by 161 MW energy error -2.1%. Underforecast blocks 69%. Worst segment: morning (9.9% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. | Heat abnormality: max temp 37.7C, +3.3C vs trailing 7d. Apparent-temperature abnormality: 36.8C, +3.7C vs trailing 7d. T+1: model overforecast on average by 163 MW energy error +2.1%. Overforecast blocks 58%. Worst segment: evening (11.6% segment MAPE). Weather was hot/humid, so overforecast points to correction stacking or baseline too high. T+2: model underforecast on average by 161 MW energy error -2.1%. Underforecast blocks 69%. Worst segment: morning (9.9% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. Actual average load was 14.9% higher than trailing 7-day level. Actual load had sharp ramp of 705 MW between 15-minute blocks. T+1 highest MAPE segment is evening; over-forecast dominates. T+2 highest MAPE segment is morning; under-forecast dominates. | Confirm whether any non-weather operational event occurred: outage, feeder shutdown, industry holiday, grid restriction, or schedule revision. | Use nonlinear cooling-load and heat-index multipliers for April-June afternoons. Track apparent temperature separately from dry-bulb temperature. Adaptive baseline should exclude anomaly days and shorten window in April-June. Apply ramp-aware forecast limit before export and monitor ramp misses. | 93.8554 | 92.7332 | 7674.7146 | 9233.71 | 37.7227 | 31.9688 | 0.19091 | 14.2091 | 49.7822
2026-04-18 | 96.27% accuracy | 97.63% accuracy | Heat abnormality: max temp 39.0C, +3.5C vs trailing 7d. Apparent-temperature abnormality: 39.4C, +5.1C vs trailing 7d. | T+1: model underforecast on average by 114 MW energy error -1.5%. Underforecast blocks 70%. Worst segment: evening (6.5% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. | T+2: model overforecast on average by 97 MW energy error +1.3%. Overforecast blocks 80%. Worst segment: evening (3.2% segment MAPE). Weather was hot/humid, so overforecast points to correction stacking or baseline too high. | Heat abnormality: max temp 39.0C, +3.5C vs trailing 7d. Apparent-temperature abnormality: 39.4C, +5.1C vs trailing 7d. T+1: model underforecast on average by 114 MW energy error -1.5%. Underforecast blocks 70%. Worst segment: evening (6.5% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. T+2: model overforecast on average by 97 MW energy error +1.3%. Overforecast blocks 80%. Worst segment: evening (3.2% segment MAPE). Weather was hot/humid, so overforecast points to correction stacking or baseline too high. Actual average load was 11.4% higher than trailing 7-day level. Actual load had sharp ramp of 768 MW between 15-minute blocks. Weekend profile can differ from weekday industrial/agricultural consumption. T+1 highest MAPE segment is evening; under-forecast dominates. |  | Use nonlinear cooling-load and heat-index multipliers for April-June afternoons. Track apparent temperature separately from dry-bulb temperature. Adaptive baseline should exclude anomaly days and shorten window in April-June. Apply ramp-aware forecast limit before export and monitor ramp misses. Keep separate weekday/weekend bias tables. | 96.2668 | 97.6294 | 7675.9753 | 9883.41 | 38.9545 | 35.6503 | 0 | 9.8182 | 52.842
2026-04-19 | 91.98% accuracy | 88.84% accuracy | Heat abnormality: max temp 38.8C, +2.3C vs trailing 7d. | T+1: model overforecast on average by 349 MW energy error +4.9%. Overforecast blocks 76%. Worst segment: morning (15.3% segment MAPE). Weather was hot/humid, so overforecast points to correction stacking or baseline too high. | T+2: model underforecast on average by 115 MW energy error -1.6%. Underforecast blocks 44%. Worst segment: morning (18.1% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. | Heat abnormality: max temp 38.8C, +2.3C vs trailing 7d. T+1: model overforecast on average by 349 MW energy error +4.9%. Overforecast blocks 76%. Worst segment: morning (15.3% segment MAPE). Weather was hot/humid, so overforecast points to correction stacking or baseline too high. T+2: model underforecast on average by 115 MW energy error -1.6%. Underforecast blocks 44%. Worst segment: morning (18.1% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. Actual load had sharp ramp of 858 MW between 15-minute blocks. Weekend profile can differ from weekday industrial/agricultural consumption. T+1 highest MAPE segment is morning; over-forecast dominates. T+2 highest MAPE segment is morning; under-forecast dominates. | Confirm whether any non-weather operational event occurred: outage, feeder shutdown, industry holiday, grid restriction, or schedule revision. | Use nonlinear cooling-load and heat-index multipliers for April-June afternoons. Track apparent temperature separately from dry-bulb temperature. Apply ramp-aware forecast limit before export and monitor ramp misses. Keep separate weekday/weekend bias tables. | 91.9795 | 88.843 | 7132.7298 | 9637.87 | 38.8364 | 29.9628 | 0 | 13.4227 | 50.4728
2026-04-20 | 94.86% accuracy | 90.30% accuracy | Heat abnormality: max temp 38.1C, +0.7C vs trailing 7d. | T+1: model underforecast on average by 322 MW energy error -4.0%. Underforecast blocks 81%. Worst segment: afternoon/ramp (10.2% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. | T+2: model underforecast on average by 749 MW energy error -9.2%. Underforecast blocks 90%. Worst segment: afternoon/ramp (13.0% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. | Heat abnormality: max temp 38.1C, +0.7C vs trailing 7d. T+1: model underforecast on average by 322 MW energy error -4.0%. Underforecast blocks 81%. Worst segment: afternoon/ramp (10.2% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. T+2: model underforecast on average by 749 MW energy error -9.2%. Underforecast blocks 90%. Worst segment: afternoon/ramp (13.0% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. Actual average load was 10.5% higher than trailing 7-day level. Actual load had sharp ramp of 667 MW between 15-minute blocks. T+1 worst error is in afternoon/ramp blocks; under-forecast dominates. T+2 worst error is in afternoon/ramp blocks; under-forecast dominates. | Confirm whether any non-weather operational event occurred: outage, feeder shutdown, industry holiday, grid restriction, or schedule revision. | Use nonlinear cooling-load and heat-index multipliers for April-June afternoons. Track apparent temperature separately from dry-bulb temperature. Adaptive baseline should exclude anomaly days and shorten window in April-June. Apply ramp-aware forecast limit before export and monitor ramp misses. Tune afternoon ramp weights around blocks 52-68. | 94.856 | 90.2974 | 8007.621 | 9957.49 | 38.1182 | 27.4157 | 0 | 16.6364 | 48.5686
2026-04-21 | 96.23% accuracy | 88.58% accuracy | Heat abnormality: max temp 38.3C, +0.2C vs trailing 7d. Wind abnormality: max wind 19.3, +5.8 vs trailing 7d. | T+1: model underforecast on average by 270 MW energy error -3.2%. Underforecast blocks 61%. Worst segment: evening (6.4% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. Wind/weather instability may have created non-normal load shape. | T+2: model underforecast on average by 988 MW energy error -11.8%. Underforecast blocks 99%. Worst segment: evening (14.5% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. Wind/weather instability may have created non-normal load shape. | Heat abnormality: max temp 38.3C, +0.2C vs trailing 7d. Wind abnormality: max wind 19.3, +5.8 vs trailing 7d. T+1: model underforecast on average by 270 MW energy error -3.2%. Underforecast blocks 61%. Worst segment: evening (6.4% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. Wind/weather instability may have created non-normal load shape. T+2: model underforecast on average by 988 MW energy error -11.8%. Underforecast blocks 99%. Worst segment: evening (14.5% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. Wind/weather instability may have created non-normal load shape. Actual average load was 10.8% higher than trailing 7-day level. Actual load had sharp ramp of 663 MW between 15-minute blocks. T+1 highest MAPE segment is evening; under-forecast dominates. T+2 highest MAPE segment is evening; under-forecast dominates. | Confirm whether any non-weather operational event occurred: outage, feeder shutdown, industry holiday, grid restriction, or schedule revision. | Use nonlinear cooling-load and heat-index multipliers for April-June afternoons. Track apparent temperature separately from dry-bulb temperature. Keep wind as diagnostic unless load drop is proven in backtest. Adaptive baseline should exclude anomaly days and shorten window in April-June. Apply ramp-aware forecast limit before export and monitor ramp misses. | 96.229 | 88.5814 | 8265.5749 | 10449.58 | 38.2591 | 24.1634 | 0 | 19.3273 | 47.5038
2026-04-22 | 96.30% accuracy | 90.22% accuracy | Heat abnormality: max temp 39.7C, +1.4C vs trailing 7d. | T+1: model underforecast on average by 63 MW energy error -0.7%. Underforecast blocks 78%. Worst segment: afternoon/ramp (6.3% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. | T+2: model underforecast on average by 849 MW energy error -9.8%. Underforecast blocks 98%. Worst segment: afternoon/ramp (13.5% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. | Heat abnormality: max temp 39.7C, +1.4C vs trailing 7d. T+1: model underforecast on average by 63 MW energy error -0.7%. Underforecast blocks 78%. Worst segment: afternoon/ramp (6.3% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. T+2: model underforecast on average by 849 MW energy error -9.8%. Underforecast blocks 98%. Worst segment: afternoon/ramp (13.5% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. Actual average load was 13.3% higher than trailing 7-day level. Actual load had sharp ramp of 878 MW between 15-minute blocks. T+1 worst error is in afternoon/ramp blocks; under-forecast dominates. T+2 worst error is in afternoon/ramp blocks; under-forecast dominates. | Confirm whether any non-weather operational event occurred: outage, feeder shutdown, industry holiday, grid restriction, or schedule revision. | Use nonlinear cooling-load and heat-index multipliers for April-June afternoons. Track apparent temperature separately from dry-bulb temperature. Adaptive baseline should exclude anomaly days and shorten window in April-June. Apply ramp-aware forecast limit before export and monitor ramp misses. Tune afternoon ramp weights around blocks 52-68. | 96.302 | 90.2188 | 8660.8405 | 10518.35 | 39.7136 | 26.1574 | 0 | 16.4818 | 50.1017
2026-04-23 | 96.08% accuracy | 94.36% accuracy | Heat abnormality: max temp 40.3C, +1.7C vs trailing 7d. | T+1: model underforecast on average by 254 MW energy error -2.8%. Underforecast blocks 86%. Worst segment: afternoon/ramp (7.8% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. | T+2: model underforecast on average by 26 MW energy error -0.3%. Underforecast blocks 64%. Worst segment: afternoon/ramp (6.9% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. | Heat abnormality: max temp 40.3C, +1.7C vs trailing 7d. T+1: model underforecast on average by 254 MW energy error -2.8%. Underforecast blocks 86%. Worst segment: afternoon/ramp (7.8% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. T+2: model underforecast on average by 26 MW energy error -0.3%. Underforecast blocks 64%. Worst segment: afternoon/ramp (6.9% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. Actual average load was 15.2% higher than trailing 7-day level. Actual load had sharp ramp of 533 MW between 15-minute blocks. T+1 worst error is in afternoon/ramp blocks; under-forecast dominates. T+2 worst error is in afternoon/ramp blocks; under-forecast dominates. |  | Use nonlinear cooling-load and heat-index multipliers for April-June afternoons. Track apparent temperature separately from dry-bulb temperature. Adaptive baseline should exclude anomaly days and shorten window in April-June. Apply ramp-aware forecast limit before export and monitor ramp misses. Tune afternoon ramp weights around blocks 52-68. | 96.0795 | 94.3592 | 9035.0146 | 10559 | 40.3091 | 23.4384 | 0 | 11.7909 | 49.7569
2026-04-24 | 97.46% accuracy | 94.79% accuracy | Heat abnormality: max temp 40.9C, +2.1C vs trailing 7d. Apparent-temperature abnormality: 40.6C, +2.7C vs trailing 7d. | T+1: model underforecast on average by 45 MW energy error -0.5%. Underforecast blocks 64%. Worst segment: afternoon/ramp (4.2% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. | T+2: model underforecast on average by 294 MW energy error -3.1%. Underforecast blocks 75%. Worst segment: evening (7.7% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. | Heat abnormality: max temp 40.9C, +2.1C vs trailing 7d. Apparent-temperature abnormality: 40.6C, +2.7C vs trailing 7d. T+1: model underforecast on average by 45 MW energy error -0.5%. Underforecast blocks 64%. Worst segment: afternoon/ramp (4.2% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. T+2: model underforecast on average by 294 MW energy error -3.1%. Underforecast blocks 75%. Worst segment: evening (7.7% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. Actual average load was 16.1% higher than trailing 7-day level. Actual load had sharp ramp of 499 MW between 15-minute blocks. T+1 worst error is in afternoon/ramp blocks; under-forecast dominates. T+2 highest MAPE segment is evening; under-forecast dominates. |  | Use nonlinear cooling-load and heat-index multipliers for April-June afternoons. Track apparent temperature separately from dry-bulb temperature. Adaptive baseline should exclude anomaly days and shorten window in April-June. Apply ramp-aware forecast limit before export and monitor ramp misses. Tune afternoon ramp weights around blocks 52-68. | 97.4575 | 94.7917 | 9360.6394 | 10687.15 | 40.9227 | 26.3376 | 0 | 13.2818 | 51.7008
2026-04-25 | 97.09% accuracy | 95.87% accuracy | Heat abnormality: max temp 41.0C, +1.7C vs trailing 7d. Apparent-temperature abnormality: 40.2C, +1.9C vs trailing 7d. Wind abnormality: max wind 21.1, +6.7 vs trailing 7d. | T+1: model underforecast on average by 121 MW energy error -1.2%. Underforecast blocks 69%. Worst segment: afternoon/ramp (6.3% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. Wind/weather instability may have created non-normal load shape. | T+2: model underforecast on average by 336 MW energy error -3.4%. Underforecast blocks 78%. Worst segment: afternoon/ramp (8.0% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. Wind/weather instability may have created non-normal load shape. | Heat abnormality: max temp 41.0C, +1.7C vs trailing 7d. Apparent-temperature abnormality: 40.2C, +1.9C vs trailing 7d. Wind abnormality: max wind 21.1, +6.7 vs trailing 7d. T+1: model underforecast on average by 121 MW energy error -1.2%. Underforecast blocks 69%. Worst segment: afternoon/ramp (6.3% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. Wind/weather instability may have created non-normal load shape. T+2: model underforecast on average by 336 MW energy error -3.4%. Underforecast blocks 78%. Worst segment: afternoon/ramp (8.0% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. Wind/weather instability may have created non-normal load shape. Actual average load was 15.5% higher than trailing 7-day level. Actual load had sharp ramp of 436 MW between 15-minute blocks. Weekend profile can differ from weekday industrial/agricultural consumption. T+1 worst error is in afternoon/ramp blocks; under-forecast dominates. T+2 worst error is in afternoon/ramp blocks; under-forecast dominates. |  | Use nonlinear cooling-load and heat-index multipliers for April-June afternoons. Track apparent temperature separately from dry-bulb temperature. Keep wind as diagnostic unless load drop is proven in backtest. Adaptive baseline should exclude anomaly days and shorten window in April-June. Apply ramp-aware forecast limit before export and monitor ramp misses. Keep separate weekday/weekend bias tables. Tune afternoon ramp weights around blocks 52-68. | 97.0862 | 95.8694 | 9588.7661 | 10858.15 | 41.0273 | 25.7074 | 0 | 21.0682 | 51.5743
2026-04-26 | 94.66% accuracy | 91.72% accuracy | Heat abnormality: max temp 41.0C, +1.4C vs trailing 7d. Wind abnormality: max wind 20.5, +4.5 vs trailing 7d. | T+1: model overforecast on average by 382 MW energy error +4.2%. Overforecast blocks 60%. Worst segment: morning (9.6% segment MAPE). Wind/storm conditions may have reduced load or shifted demand. | T+2: model underforecast on average by 445 MW energy error -4.9%. Underforecast blocks 76%. Worst segment: night (11.0% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. Wind/weather instability may have created non-normal load shape. | Heat abnormality: max temp 41.0C, +1.4C vs trailing 7d. Wind abnormality: max wind 20.5, +4.5 vs trailing 7d. T+1: model overforecast on average by 382 MW energy error +4.2%. Overforecast blocks 60%. Worst segment: morning (9.6% segment MAPE). Wind/storm conditions may have reduced load or shifted demand. T+2: model underforecast on average by 445 MW energy error -4.9%. Underforecast blocks 76%. Worst segment: night (11.0% segment MAPE). Likely missed nonlinear cooling demand from heat/apparent-temperature. Wind/weather instability may have created non-normal load shape. Actual average load was 5.7% higher than trailing 7-day level. Actual load had sharp ramp of 549 MW between 15-minute blocks. Weekend profile can differ from weekday industrial/agricultural consumption. T+1 highest MAPE segment is morning; over-forecast dominates. T+2 error concentrated in night blocks; under-forecast bias visible. | Confirm whether any non-weather operational event occurred: outage, feeder shutdown, industry holiday, grid restriction, or schedule revision. | Use nonlinear cooling-load and heat-index multipliers for April-June afternoons. Track apparent temperature separately from dry-bulb temperature. Keep wind as diagnostic unless load drop is proven in backtest. Adaptive baseline should exclude anomaly days and shorten window in April-June. Apply ramp-aware forecast limit before export and monitor ramp misses. Keep separate weekday/weekend bias tables. Maintain dedicated T+2 night correction for blocks 1-32. | 94.6571 | 91.7233 | 9066.0346 | 10635.11 | 40.9545 | 25.8314 | 0 | 20.4773 | 51.5337
2026-04-27 | 90.55% accuracy | 85.96% accuracy | Heat abnormality: max temp 41.1C, +1.2C vs trailing 7d. Apparent-temperature abnormality: 40.5C, +1.7C vs trailing 7d. Wind abnormality: max wind 22.1, +5.1 vs trailing 7d. | T+1: model overforecast on average by 625 MW energy error +6.7%. Overforecast blocks 51%. Worst segment: evening (34.5% segment MAPE). Wind/storm conditions may have reduced load or shifted demand. | T+2: model overforecast on average by 405 MW energy error +4.4%. Overforecast blocks 54%. Worst segment: evening (31.2% segment MAPE). Wind/storm conditions may have reduced load or shifted demand. | Heat abnormality: max temp 41.1C, +1.2C vs trailing 7d. Apparent-temperature abnormality: 40.5C, +1.7C vs trailing 7d. Wind abnormality: max wind 22.1, +5.1 vs trailing 7d. T+1: model overforecast on average by 625 MW energy error +6.7%. Overforecast blocks 51%. Worst segment: evening (34.5% segment MAPE). Wind/storm conditions may have reduced load or shifted demand. T+2: model overforecast on average by 405 MW energy error +4.4%. Overforecast blocks 54%. Worst segment: evening (31.2% segment MAPE). Wind/storm conditions may have reduced load or shifted demand. Actual average load was 4.7% higher than trailing 7-day level. Actual load had sharp ramp of 1442 MW between 15-minute blocks. T+1 highest MAPE segment is evening; over-forecast dominates. T+2 highest MAPE segment is evening; over-forecast dominates. | Confirm whether any non-weather operational event occurred: outage, feeder shutdown, industry holiday, grid restriction, or schedule revision. | Use nonlinear cooling-load and heat-index multipliers for April-June afternoons. Track apparent temperature separately from dry-bulb temperature. Keep wind as diagnostic unless load drop is proven in backtest. Adaptive baseline should exclude anomaly days and shorten window in April-June. Apply ramp-aware forecast limit before export and monitor ramp misses. | 90.5476 | 85.9598 | 9269.6598 | 10455.58 | 41.1182 | 24.8421 | 0.21364 | 22.1318 | 51.3328
2026-04-28 | No forecast blocks | No forecast blocks | Heat abnormality: max temp 39.2C, +-1.2C vs trailing 7d. | T+1: no block-level forecast rows available; daily summary only. | T+2: no block-level forecast rows available; daily summary only. | Heat abnormality: max temp 39.2C, +-1.2C vs trailing 7d. T+1: no block-level forecast rows available; daily summary only. T+2: no block-level forecast rows available; daily summary only. Actual average load was 69.0% lower than trailing 7-day level. Actual load had sharp ramp of 8580 MW between 15-minute blocks. No block-level forecast rows available in workbook for this date; only daily summary is available. |  | Use nonlinear cooling-load and heat-index multipliers for April-June afternoons. Track apparent temperature separately from dry-bulb temperature. Adaptive baseline should exclude anomaly days and shorten window in April-June. Apply ramp-aware forecast limit before export and monitor ramp misses. |  |  | 2804.259 | 10141.15 | 39.15 | 31.7633 | 0.0090909 | 14.8773 | 51.5853
2026-04-29 | No forecast blocks | No forecast blocks | Humidity abnormality: mean humidity 35.5%, +9.2 points vs trailing 7d. | T+1: no block-level forecast rows available; daily summary only. | T+2: no block-level forecast rows available; daily summary only. | Humidity abnormality: mean humidity 35.5%, +9.2 points vs trailing 7d. T+1: no block-level forecast rows available; daily summary only. T+2: no block-level forecast rows available; daily summary only. No block-level forecast rows available in workbook for this date; only daily summary is available. |  | Treat humidity as a heat-load amplifier, not only a standalone linear feature. |  |  |  |  | 37.1364 | 35.4557 | 0 | 13.9909 | 50.3033